## Tabelle1
Line excluded / Switch Position (True = closed) | [F, F, F] | [T,F,F] | [F,T,F] | [F,F,T] | [T,T,F] | [T,F,T] | [F,T,T] | [T,T,T] | Conclusion
0 (Line 1-2) | Feeder 1 not supplied | Max voltage 1.03, Min voltage 0.8981237610445258, Max line loading 83.71066061002337 | Feeder 1 not supplied | Feeder 1 not supplied | Max voltage 1.03, Min voltage 0.9041539498157142, Max line loading 83.49817296370603 | Max voltage 1.03, Min voltage 0.9006772938777127, Max line loading 83.62745862094197 | Feeder 1 not supplied | Max voltage 1.03, Min voltage 0.9047285880152508, Max line loading 83.4859534898267 | Switch S1 should be closed to supply Feeder 1, no configuration stays within the 5% bus limits, all closed seems to be the best
1 (Line 2-3) | Feeder 1 not supplied | Max voltage 1.03, Min voltage 0.8967954043531018, Max line loading 84.15920642566458 | Feeder 1 not supplied | Feeder 1 not supplied | Max voltage 1.03, Min voltage 0.9029061827506065, Max line loading 83.94449367130781 | Max voltage 1.03, Min voltage 0.8994396325360939, Max line loading 84.07532600793662 | Feeder 1 not supplied | Max voltage 1.03, Min voltage 0.9035228369291675, Max line loading 83.93225563641445 | Switch S1 should be closed to supply Feeder 1, but no configuration stays within the 5% bus limits, all closed seems to be the best
2 (Line 3-4) | "Left side" of Feeder 1 not supplied (Bus 4-6) | "Left side" of Feeder 1 not supplied (Bus 4-6) | Max voltage 1.03, Min voltage 0.9097941700084861, Max line loading 98.06329252619408 | Max voltage 1.03, Min voltage 0.9082680976694808, Max line loading 98.23658103397986 | Max voltage 1.03, Min voltage 0.9479417117997437, Max line loading 49.387264337203334 | Max voltage 1.03, Min voltage 0.9466233055885018, Max line loading 69.0849231575195 | Max voltage 1.03, Min voltage 0.914905452963205, Max line loading 97.89575747796687 | Max voltage 1.03, Min voltage 0.9526957975661646, Max line loading 49.32456017766225 | Close all switches
3 (Line 4-5) | "Lower left side" of Feeder 1 not supplied (Bus 5-6) | "Lower left side" of Feeder 1 not supplied (Bus 5-6) | Max voltage 1.03, Min voltage 0.9146571169897459, Max line loading 97.61383605681601 | "Lower left side" of Feeder 1 not supplied (Bus 5-6) | Max voltage 1.03, Min voltage 0.9516862323942955, Max line loading 49.86427513310964 | "Lower left side" of Feeder 1 not supplied (Bus 5-6) | Max voltage 1.03, Min voltage 0.9188712521251743, Max line loading 97.18058052453536 | Max voltage 1.03, Min voltage 0.9527300742671277, Max line loading 50.89388009678078 | Definitely close S1 and S2, closing S3 optional
4 (Line 5-6) | Bus 6 not supplied | Bus 6 not supplied | Max voltage 1.03, Min voltage 0.9209853604852769, Max line loading 97.29219913308698 | Bus 6 not supplied | Max voltage 1.03, Min voltage 0.9566623454619723, Max line loading 50.84509230230062 | Bus 6 not supplied | Max voltage 1.03, Min voltage 0.9242735436168298, Max line loading 97.05242786898366 | Max voltage 1.03, Min voltage 0.957462526495259, Max line loading 51.40974770477743 | Definitely close S1 and S2, closing S3 optional
5 (Line 7-8) | Bus 7 not supplied | Bus 7 not supplied | Max voltage 1.03, Min voltage 0.9226095293609714, Max line loading 97.19010611915036 | Bus 7 not supplied | Max voltage 1.03, Min voltage 0.9556426321453336, Max line loading 51.758815120519486 | Bus 7 not supplied | Max voltage 1.03, Min voltage 0.924407396907508, Max line loading 97.07096071651745 | Max voltage 1.03, Min voltage 0.9551535912807486, Max line loading 51.90385104440648 | Definitely close S1 and S2, closing S3 optional
6 (Line 8-9) | Bus 9-11 not supplied | Bus 9-11 not supplied | Bus 9-11 not supplied | Max voltage 1.03, Min voltage 0.9236965406856544, Max line loading 96.97471161032757 | Bus 9-11 not supplied | Max voltage 1.03, Min voltage 0.9521123183860455, Max line loading 68.83070998943113 | Max voltage 1.03, Min voltage 0.9242571122618068, Max line loading 96.91784879068757 | Max voltage 1.03, Min voltage 0.9539326237799826, Max line loading 52.581646328219186 | Close all switches
7 (Line 9-10) | Bus 10-11 not supplied | Bus 10-11 not supplied | Bus 10-11 not supplied | Max voltage 1.03, Min voltage 0.9252280587316913, Max line loading 96.93599753186312 | Bus 10-11 not supplied | Max voltage 1.03, Min voltage 0.9545374689677428, Max line loading 55.250830541014594 | Max voltage 1.03, Min voltage 0.9261242860295411, Max line loading 96.91954785382819 | Max voltage 1.03, Min voltage 0.9573505717917183, Max line loading 51.898491229983435 | Close all switches
8 (Line 10-11) | Bus 11 not supplied | Bus 11 not supplied | Bus 11 not supplied | Max voltage 1.03, Min voltage 0.9245763973195269, Max line loading 96.9191358268074 | Bus 11 not supplied | Max voltage 1.03, Min voltage 0.95584332869108, Max line loading 52.01142610963569 | Max voltage 1.03, Min voltage 0.924593600356177, Max line loading 96.91739218659127 | Max voltage 1.03, Min voltage 0.9581224531303263, Max line loading 51.319809191319735 | Close all switches
9 (Line 3-8) | Bus 7-11 not supplied | Max voltage 1.03, Min voltage 0.9496324317722648, Max line loading 47.00342244212042 | Max voltage 1.03, Min voltage 0.9013231781080892, Max line loading 98.63652971754352 | Max voltage 1.03, Min voltage 0.9196149975963827, Max line loading 97.39962755055112 | Max voltage 1.03, Min voltage 0.9543432410879351, Max line loading 48.64934722607964 | Max voltage 1.03, Min voltage 0.9561444537837639, Max line loading 51.56945484087245 | Max voltage 1.03, Min voltage 0.9209952353246988, Max line loading 97.37814197438045 | Max voltage 1.03, Min voltage 0.9576648942333785, Max line loading 50.786932399511585 | Definitely close S1, closing S2 and S3 optional
10 (Line 12-13) | Bus 13-14 not supplied (Feeder 2) | Max voltage 1.03, Min voltage 0.9076205658776388, Max line loading 112.31808036414823 | Bus 13-14 not supplied (Feeder 2) | Bus 13-14 not supplied (Feeder 2) | Max voltage 1.03, Min voltage 0.9082987718426515, Max line loading 112.3016673478318 | Max voltage 1.03, Min voltage 0.9107454554033548, Max line loading 112.08754040177944 | Bus 13-14 not supplied (Feeder 2) | Max voltage 1.03, Min voltage 0.9106186590532883, Max line loading 112.0800278776313 | Line loading exceeded in any case
11 (Line 13-14) | Bus 14 not supplied | Max voltage 1.03, Min voltage 0.9085943450248039, Max line loading 111.37175910203496 | Bus 14 not supplied | Bus 14 not supplied | Max voltage 1.03, Min voltage 0.9092460684150115, Max line loading 111.35669653151339 | Max voltage 1.03, Min voltage 0.9120018634446111, Max line loading 111.14845633006858 | Bus 14 not supplied | Max voltage 1.03, Min voltage 0.9118686946513301, Max line loading 111.14058006165651 | Line loading exceeded in any case
12 (Line 6-7, Switch S2) | Max voltage 1.03, Min voltage 0.9228991593964374, Max line loading 96.99206745930469 | Max voltage 1.03, Min voltage 0.956502710532949, Max line loading 51.54444882365794 | Max voltage 1.03, Min voltage 0.9228991593964374, Max line loading 96.99206745930469 | Max voltage 1.03, Min voltage 0.9254119518783372, Max line loading 96.8597080220761 | Max voltage 1.03, Min voltage 0.956502710532949, Max line loading 51.54444882365794 | Max voltage 1.03, Min voltage 0.9559164365283743, Max line loading 51.74597897359442 | Max voltage 1.03, Min voltage 0.9254119518783372, Max line loading 96.8597080220761 | Max voltage 1.03, Min voltage 0.9559164365283743, Max line loading 51.74597897359442 | Close S1, S2 optional, Q: Why don't we close S1 in the normal operation (with all lines included), since this is basically the same scenario as here (the excluded line being a switch-line that by default is open aka not used)?
13 (Line 11-4, Switch S3) | Max voltage 1.03, Min voltage 0.9227736360932687, Max line loading 97.02690879483636 | Max voltage 1.03, Min voltage 0.9564939125065715, Max line loading 51.55649846807447 | Max voltage 1.03, Min voltage 0.9230463416590863, Max line loading 97.02445226369314 | Max voltage 1.03, Min voltage 0.9227736360932687, Max line loading 97.02690879483636 | Max voltage 1.03, Min voltage 0.9570569170047972, Max line loading 51.02203634546628 | Max voltage 1.03, Min voltage 0.9564939125065715, Max line loading 51.55649846807447 | Max voltage 1.03, Min voltage 0.9230463416590863, Max line loading 97.02445226369314 | Max voltage 1.03, Min voltage 0.9570569170047972, Max line loading 51.02203634546628 | Close S1, S2 and S3 optional, Q: Why don't we close S1 in the normal operation (with all lines included), since this is basically the same scenario as here (the excluded line being a switch-line that by default is open aka not used)?
14 (Line 14-8, Switch S1) | Max voltage 1.03, Min voltage 0.922979775268006, Max line loading 96.95880689639247 | Max voltage 1.03, Min voltage 0.922979775268006, Max line loading 96.95880689639247 | Max voltage 1.03, Min voltage 0.9232480024481036, Max line loading 96.95639477300986 | Max voltage 1.03, Min voltage 0.9255119998982649, Max line loading 96.82655817739982 | Max voltage 1.03, Min voltage 0.9232480024481036, Max line loading 96.95639477300986 | Max voltage 1.03, Min voltage 0.9255119998982649, Max line loading 96.82655817739982 | Max voltage 1.03, Min voltage 0.9264387643524712, Max line loading 96.81184540881877 | Max voltage 1.03, Min voltage 0.9264387643524712, Max line loading 96.81184540881877 | Switch positions does not matter too much, potentially critical for the 5% limits (but also the same as the default if we do not close any of the three switches)