## Slide 1: MJ2505: PRO1 Presentation
Group 9
October 26, 20222

## Slide 2: Step 1.1: Initial state of the network
Add picture of network + some facts (n_lines,…)
Colormap/bar plot to show loadings etc.

## Slide 3: CIGRE Network
Initial configuration:
18 loads
  load 0 and 10 connected to bus 1
  load 8 and 15 connected to bus 12
8 switches (3 manual)
15 lines
2 trafos
15 buses

## Slide 4: Running a power flow
Notes: Lines bus 1-2, bus 2-3 are closest to 100% (96% max)
Trafo 1 is overloaded

## Slide 5: Step 1.2: N-1 analysis
Explain procedure
Highlight critical cases and show results -> bar plot or colormap
Summarize results -> these are the cases we will consider in 3.3/3.4 -> also consider our „conclusion“ for the switches
for both: 5 and 10 % limits

## Slide 6: N-1 analysis
Went through all 120 scenarios (one line exluded + certain switch position)
Configuration reasonable?
Do some buses/lines exceed the limits?
  If yes, which/how many?

## Slide 7: N-1 analysis: critical cases
Excluding line 0:
closing all switches
max line loading = 83%
overloaded trafo
12 buses below 0.95, all above 0.9

## Slide 8: N-1 analysis: critical cases
Excluding line 1:
closing all switches
max line loading = 84%
overloaded trafo
11 buses below 0.95, all above 0.9

## Slide 9: N-1 analysis: critical cases
Excluding line 10:
leads to overloaded lines and trafo for all switch configurations
11 buses are below 0.95, all above 0.9
need to close S1 to supply Feeder 2

## Slide 10: N-1 analysis: critical cases
Excluding line 11:
leads to overloaded lines and trafo for all switch configurations
10 buses below 0.95, all above 0.9
need to close S1 to supply Feeder 2

## Slide 11: N-1 analysis: critical cases
Excluding line 14 (switch S1):
basically the same as the inital state of the network (overloaded trafo)
no critical lines
9 buses below 0.95, all above 0.9
switch configuration negligble

## Slide 12: N-1 analysis: Summary
Focus on two very critical scenarios
  Line 0 or 1 excluded -> Feeder 1 not supplied unless S1 is closed
  Line 10 or 11 excluded -> Feeder 2 not supplied unless S1 is closed
  Close all switches in these scenarios
Excluding line 14 not as big of a problem when considering timeseries
Notes: 0 and 1 are very similar
10 and 11 are very similar

## Slide 13: Step 2: Adding CS
Add explanation for initial trafo placement and size
Show results of step 2 -> network picture, colormap of peak hour, subplot-plot
Add some conclusion

## Slide 14: Different cases
Max case
  Start with some location and highest power trafos
  Go through steps 3 and 4
Iterate positions and power of the transformars based on results

## Slide 15: Adding CS
Connected to buses 2, 6, 8, 11, 13
Start with all at highest available power (0.63 MVA)
Notes: 2 instead of 3 due to critical case
Evenly distributed around the grid
6, 8, 11 are in residential areas

## Slide 16: Adding CS
At peak hour = 12:
Notes: Adding the CS without any load does not change anything for the existing buses/lines

## Slide 17: Step 3: Adding EVs
Choose peak day and convert to hourly
Set number of EVs, randomly pick profiles and add them together based on given allocation
With all lines:
  results for some n_ev
  results for max n_ev
In N-1 case:
  consider critical scenarios as in 1.2
  results for max n_ev
  results for max_n-1 case
Explain the results

## Slide 18: Adding EVs: Preparation
10-minute interval charging profiles, full year
1-hour interval charging profiles, full year
1-hour interval charging profiles, peak_day
pick max value per hour
pick day with max sum(all loads that day)
day_id = 199 => 19.07.

## Slide 19: Adding EVs: Allocation
Choose n_ev and n_ev_cs
  e.g. n_ev = 100, n_ev_cs = [10,20,30,15,25]
Randomly pick n_ev profiles (without repetitions if n_ev < 349)
Allocate the first n_ev_cs[0] to CS1 and so on
Allocate = sum loadshapes of all profiles and a load with that loadshape to the low voltage bus of the corresponding CS

## Slide 20: Adding EVs: Checking critical N-1 cases
For lines 0, 10
Remove line
Close all switches, n_ev = max n_ev
Run time series
Collect results and adjust n_ev

## Slide 21: Adding 300 EVs

## Slide 22: Adding max EVs
Case 1: increase and leave evenly distributed
Case 2: distributed oddly

## Slide 23: N-1 for max n_ev

## Slide 24: N-1 with decreased n_ev to stay within limits

## Slide 25: Step 4: 115% case
Add 115% of Evs
Check results to find weak links (without any modification)
How can we improve the network? Why is that reasonable? What are the results after the improvement?
  Choose different profiles / load optimization
  Reinforce grid
  Change transformers